## Sheet1
Tested new hardware 2.0 on delta powerline configuration
| Summary: | New hardware 2.0 was tested on 15 boards
| Date: | 5.9.2019
| Powerline position: | Delta Powerline Transmission Configuration
| Software: | 1.3
| Hardware: | 2 | [11 empty] | Symbol Index:
| Boards ID: | From 201 to 215 (together 15 boards) | [11 empty] | U1 | Measured Voltage Left Antenna
[14 empty] | U2 | Measured Voltage Right Antenna
| Test: | All boards was placed one by one under polygon 20kV powerline and
|  | with sequence shutting down powerline wires, we measured average voltage | [11 empty] | Uavg | Average Voltage |  | (U1+U2)/2
and angle difference between angle1 and angle2.
|  | Measured values from Alisa was read from LCD display. | [11 empty] | ANG1 | Measured Angle Left Antenna
| Result: | All measured values were in expected range. | [11 empty] | ANG2 | Measured Angle Right Antenna
|  | Board ID 207, LCD display did not work and for that was not tested on polygon. | [11 empty] | ANGdiff | Angle difference |  | abs(ANG1 – ANG2)
[6 empty] | Measurement 1 |  | Measurement 2 |  | Measurement 3 |  | Measurement 4 |  | Measurement 5 |  | Measurement 6 |  | Measurement 7 |  | Measurement 8 |  | Measurement 9 |  | Measurement 10 |  | Measurement 11 |  | Measurement 12 |  | Measurement 13 |  | Measurement 14
|  |  | Boards ID: |  |  | 201 |  | 215 |  | 202 |  | 203 |  | 204 |  | 205 |  | 206 |  | 208 |  | 209 |  | 210 |  | 211 |  | 212 |  | 213 |  | 214
|  |  | Left | Middle | Right | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff | Uavg | ANGdiff
|  |  | 10kV | 10kV | 10kV | 201 | 31 | 144 | 27
|  |  | X | 10kV | 10kV | 172 | 3 | 160 | 7
|  |  | 10kV | X | 10kV | 265 | 26 | 380 | 25
|  |  | 10kV | 10kV | X | 231 | 7 | 336 | 7
|  |  | X | X | 10kV | 193 | 2 | 235 | 6
|  |  | X | 10kV | X | 130 | 2 | 132 | 3
|  |  | 10kV | X | X | 130 | 6 | 427 | 1
|  |  | 20kV | 20kV | 20kV | 338 | 43 | 422 | 25 | 462 | 25 | 446 | 37 | 425 | 36 | 417 | 46 | 420 | 40 | 449 | 34 | 370 | 29 | 382 | 33 | 446 | 33 | 419 | 33 | 474 | 37 | 441 | 40
|  |  | X | 20kV | 20kV | 404 | 2 | 419 | 8 | 445 | 8 | 465 | 6 | 454 | 11 | 498 | 8 | 475 | 10 | 479 | 4 | 386 | 4 | 471 | 6 | 500 | 7 | 472 | 7 | 420 | 11 | 484 | 7
|  |  | 20kV | X | 20kV | 679 | 32 | 702 | 33 | 748 | 31 | 743 | 32 | 721 | 36 | 718 | 40 | 725 | 38 | 721 | 35 | 704 | 32 | 723 | 34 | 718 | 35 | 725 | 26 | 683 | 31 | 725 | 38
|  |  | 20kV | 20kV | X | 657 | 10 | 713 | 13 | 749 | 8 | 471 | 11 | 713 | 12 | 701 | 7 | 725 | 10 | 722 | 10 | 723 | 12 | 709 | 12 | 752 | 10 | 712 | 9 | 717 | 12 | 728 | 10
|  |  | X | X | 20kV | 516 | 6 | 514 | 2 | 537 | 6 | 573 | 1 | 553 | 3 | 581 | 3 | 573 | 1 | 578 | 1 | 522 | 2 | 563 | 3 | 587 | 1 | 555 | 4 | 532 | 6 | 582 | 2
|  |  | X | 20kV | X | 221 | 2 | 273 | 3
|  |  | 20kV | X | X | 794 | 1 | 811 | 1
|  |  | X | X | X | 0 | 0 | 0 | 0